## Pumps
Change Data only in shaded cells. Other cells may contain formulas.
Works with any set of consistent units. Optional: Note the units you are using.
Flow Units
Pressure or Head Units
math behind the calcs:
System | Curve
0 | flow almost always starts at 0, leave as is | [5 empty] | h, x of vertex, almost always 0
0 | pressure at zero flow, usually 0, sometimes a net elevation head | [5 empty] | k, y of vertex, usually 0
300 | flow at a known point on system curve | [5 empty] | r, x of known point on parabola
6 | pressure at a known point on system curve | [5 empty] | s, y of known point on parabola
1.852 | n, exponent, see commentary tab |  |  | 0.53996 | 1/n |  | n, exponent in system p=c*flow^n
[6 empty] | 0.00015507 | a=(s-k)/(r-h)^n
Pump | Curve
0 | flow at top dead head, usually 0 | [5 empty] | h, x of vertex, often 0
30 | pressure at top dead head | [5 empty] | k, y of vertex, usually high
400 | flow at a known point on pump curve | [5 empty] | r, x of known point on parabola
20 | pressure at a known point on pump curve | [5 empty] | s, y of known point on parabola
1.852 | n, exponent, see commentary tab |  |  | 0.53996 | 1/n |  | n, exponent in pump p=c*flow^n
[6 empty] | -0.0001517 | a=(s-k)/(r-h)^n
Set intervals of flow to best include flow of interest. | [6 empty] | y=(a*(x-h)^n)+k
50 | < set intervals of flow
1.2 | < multiplier for sys curve max
| System Curve | Pump Curve | Two Parallel Pumps Curve
Flow | Pressure | Pressure | Pressure
0 | 0 | 30 | 30
50 | 0.21728 | 29.7874 | 29.9411
100 | 0.78437 | 29.2327 | 29.7874
150 | 1.662 | 28.3741 | 29.5496
200 | 2.8316 | 27.2299 | 29.2327
250 | 4.2806 | 25.8124 | 28.84
300 | 6 | 24.1303 | 28.3741
350 | 7.9825 | 22.1909 | 27.8368
400 | 10.222 | 20 | 27.2299
450 | 12.7137 | 17.5625 | 26.5547
500 | 15.4531 | 14.8826 | 25.8124
550 | 18.4363 | 11.9642 | 25.0039
600 | 21.66 | 8.8105 | 24.1303
650 | 25.1211 | 5.4246 | 23.1924
700 | 28.8167 | 1.8093 | 22.1909
750 | 32.7443 | #N/A | 21.1266
800 | #N/A | #N/A | 20
850 | #N/A | #N/A | 18.8118
900 | #N/A | #N/A | 17.5625
950 | #N/A | #N/A | 16.2526

## Fans
Change Data only in shaded cells. Other cells may contain formulas.
Works with any set of consistent units. Optional: Note the units you are using.
Flow Units
Pressure or Head Units
math behind the calcs:
System | Curve
0 | flow almost always starts at 0, leave as is | [5 empty] | h, x of vertex, almost always 0
0 | pressure at zero flow, usually 0, sometimes a net elevation head | [5 empty] | k, y of vertex, usually 0
500 | flow at a known point on system curve | [5 empty] | r, x of known point on parabola
0.25 | pressure at a known point on system curve | [5 empty] | s, y of known point on parabola
2 | n, exponent, see commentary tab |  |  | 0.5 | 1/n |  | n, exponent in system p=c*flow^n
[6 empty] | 1e-06 | a=(s-k)/(r-h)^n
Fan | Curve
0 | flow at top dead head, usually 0 | [5 empty] | h, x of vertex, often 0
0.75 | pressure at top dead head | [5 empty] | k, y of vertex, usually high
600 | flow at a known point on fan curve | [5 empty] | r, x of known point on parabola
0.3 | pressure at a known point on fan curve | [5 empty] | s, y of known point on parabola
2 | n, exponent, see commentary tab |  |  | 0.5 | 1/n |  | n, exponent in fan p=c*flow^n
[6 empty] | -1.25e-06 | a=(s-k)/(r-h)^n
Set intervals of flow to best include flow of interest. | [6 empty] | y=(a*(x-h)^n)+k
50 | < set intervals of flow
1.2 | < multiplier for sys curve max
| System Curve | Fan Curve | Two Parallel Fans Curve
Flow | Pressure | Pressure | Pressure
0 | 0 | 0.75 | 0.75
50 | 0.0025 | 0.74687 | 0.74922
100 | 0.01 | 0.7375 | 0.74687
150 | 0.0225 | 0.72188 | 0.74297
200 | 0.04 | 0.7 | 0.7375
250 | 0.0625 | 0.67188 | 0.73047
300 | 0.09 | 0.6375 | 0.72188
350 | 0.1225 | 0.59688 | 0.71172
400 | 0.16 | 0.55 | 0.7
450 | 0.2025 | 0.49687 | 0.68672
500 | 0.25 | 0.4375 | 0.67188
550 | 0.3025 | 0.37187 | 0.65547
600 | 0.36 | 0.3 | 0.6375
650 | 0.4225 | 0.22187 | 0.61797
700 | 0.49 | 0.1375 | 0.59688
750 | 0.5625 | 0.046875 | 0.57422
800 | 0.64 | #N/A | 0.55
850 | 0.7225 | #N/A | 0.52422
900 | 0.81 | #N/A | 0.49687
950 | #N/A | #N/A | 0.46797

## Commentary
Commentary
This spreadsheet is for estimating only. Always use more rigorous methods for important work.
The spreadsheet creates parabola curves that estimate the system curve and the pump or fan curves.
This is a formula method. A formula method is usually not accurate over an entire range of flows, particularly where the range passes from laminar flow to turbulent flow. However in many practical problems, the range of interest is usually turbulent flow only
If you need to be more accurate within this spreadsheet, obtain actual system curves, pump curves, and fan curves through other methods and resources. Attempt to get these spreadsheet curves to approximate your actual curves, by varying the exponent n, or by giving data for a different representative point on the curve.
n, the exponent in pressure=c(constant)*flow^n, can be set by the user, for both the system curve and the pump or fan curve.
For liquid / pump systems, the Hazen-Williams formula exponent is 1.852, and is the default entry. However, the Darcy-Weisbach formula exponent is 2.
For air / fan systems, the drag formula exponent is 2, and is the default entry.
The "multiplier for sys curve max" is used to keep the graph from being much taller than the pump or fan data. The default entry is 1.2